## Server Power
Machine Name | Server 1 : ThinkSystem SR675 V3 3yr Warranty with Controlled GPU | Model | 7D9RCTO1WW | Quantity | 1
Power Summary |  |  | Idle | Load Factor | Nominal Max | Worst Case Max
Operating Voltage | 230V | Input Power (W) | 910.1 | 2,645.2 | 4,483.7 | 4,824.6
Load Factor (%) | 70.0 | Input Current (A) | 4.8 | 11.8 | 19.8 | 21.3
System S5 (W) | 12.0 | Apparent Power (VA) | 1,095.2 | 2,718.6 | 4,556.6 | 4,893.1
Power Policy | N+1 redundancy with over-subscription | Heat Generation (BTU/Hr) | 3,105.3 | 9,025.5 | 15,298.4 | 16,461.5
Power Utilization | 49.25% | Power(DC W) | 687.4 | 2,497.5 | 4,278.8 | 4,609.5
Machine Name | Server 2 : ThinkSystem SR675 V3 3yr Warranty with Controlled GPU | Model | 7D9RCTO1WW | Quantity | 1
Power Summary |  |  | Idle | Load Factor | Nominal Max | Worst Case Max
Operating Voltage | 230V | Input Power (W) | 2,104.9 | 4,850.4 | 7,622.3 | 7,686.0
Load Factor (%) | 70.0 | Input Current (A) | 9.5 | 21.4 | 33.5 | 33.8
System S5 (W) | 12.0 | Apparent Power (VA) | 2,183.5 | 4,919.3 | 7,699.2 | 7,763.7
Power Policy | N+1 redundancy with over-subscription | Heat Generation (BTU/Hr) | 7,182.0 | 16,549.6 | 26,007.1 | 26,224.8
Power Utilization | 78.09% | Power(DC W) | 1,977.4 | 4,634.2 | 7,248.8 | 7,309.5
Machine Name | Server 3 : ThinkSystem SR675 V3 3yr Warranty with Controlled GPU | Model | 7D9RCTO1WW | Quantity | 1
Power Summary |  |  | Idle | Load Factor | Nominal Max | Worst Case Max
Operating Voltage | 230V | Input Power (W) | 496.1 | 1,541.9 | 2,593.8 | 2,932.6
Load Factor (%) | 70.0 | Input Current (A) | 2.5 | 6.9 | 11.4 | 12.9
System S5 (W) | 12.0 | Apparent Power (VA) | 563.8 | 1,578.2 | 2,620.0 | 2,962.2
Power Policy | Non-Redundant | Heat Generation (BTU/Hr) | 1,692.8 | 5,261.1 | 8,850.0 | 10,005.9
Power Utilization | 57.29% | Power(DC W) | 419.3 | 1,434.9 | 2,434.4 | 2,749.9
Machine Name | Server 4 : ThinkSystem SR675 V3 3yr Warranty with Controlled GPU | Model | 7D9RCTO1WW | Quantity | 1
Power Summary |  |  | Idle | Load Factor | Nominal Max | Worst Case Max
Operating Voltage | 230V | Input Power (W) | 671.9 | 1,908.0 | 3,210.0 | 3,539.2
Load Factor (%) | 70.0 | Input Current (A) | 3.5 | 8.5 | 14.2 | 15.6
System S5 (W) | 12.0 | Apparent Power (VA) | 794.2 | 1,961.0 | 3,262.2 | 3,585.8
Power Policy | Non-Redundant | Heat Generation (BTU/Hr) | 2,292.5 | 6,510.1 | 10,952.4 | 12,075.7
Power Utilization | 46.08% | Power(DC W) | 523.4 | 1,772.7 | 3,002.1 | 3,317.7
Machine Name | Server 5 : ThinkSystem SR650 V3 3yr warranty with Controlled GPU | Model | 7D76CTOEWW | Quantity | 1
Power Summary |  |  | Idle | Load Factor | Nominal Max | Worst Case Max
Operating Voltage | 230V | Input Power (W) | 175.3 | 641.3 | 1,083.7 | 1,193.8
Load Factor (%) | 70.0 | Input Current (A) | 0.8 | 3.1 | 5.1 | 5.6
System S5 (W) | 12.0 | Apparent Power (VA) | 192.6 | 704.8 | 1,169.0 | 1,279.5
Power Policy | N+N redundancy with over-subscription | Heat Generation (BTU/Hr) | 598.1 | 2,188.3 | 3,697.5 | 4,073.1
Power Utilization | 52.22% | Power(DC W) | 155.9 | 592.1 | 1,021.4 | 1,127.9
Machine Name | Server 6 : ThinkSystem SR650 V3 3yr warranty with Controlled GPU | Model | 7D76CTOEWW | Quantity | 1
Power Summary |  |  | Idle | Load Factor | Nominal Max | Worst Case Max
Operating Voltage | 230V | Input Power (W) | 208.4 | 791.1 | 1,356.7 | 1,487.1
Load Factor (%) | 70.0 | Input Current (A) | 1.0 | 3.8 | 6.3 | 6.8
System S5 (W) | 12.0 | Apparent Power (VA) | 229.0 | 868.4 | 1,441.7 | 1,567.0
Power Policy | N+N redundancy with over-subscription | Heat Generation (BTU/Hr) | 711.1 | 2,699.4 | 4,628.9 | 5,074.0
Power Utilization | 65.44% | Power(DC W) | 186.0 | 739.9 | 1,285.0 | 1,413.4
Machine Name | Server 7 : ThinkSystem SR650a V4 - 3yr Warranty | Model | 7DGDCTO2WW | Quantity | 1
Power Summary |  |  | Idle | Load Factor | Nominal Max | Worst Case Max
Operating Voltage | 230V | Input Power (W) | 342.3 | 1,315.4 | 2,297.8 | 2,618.1
Load Factor (%) | 70.0 | Input Current (A) | 1.9 | 5.8 | 10.1 | 11.5
System S5 (W) | 12.0 | Apparent Power (VA) | 434.4 | 1,332.7 | 2,316.3 | 2,633.9
Power Policy | N+N redundancy without over-subscription | Heat Generation (BTU/Hr) | 1,167.9 | 4,488.0 | 7,840.1 | 8,932.9
Power Utilization | 90.53% | Power(DC W) | 243.6 | 1,196.0 | 2,133.2 | 2,444.2
Note on E2: All power management features are enabled in UEFI and the operating system. Server is booted to operating system and sitting idle for several minutes.
Note on F2: Typical long term power consumption under nominal conditions with no faults and user selected load factor.
Note on G2: Typical long term power consumption under nominal conditions with no faults and 100% load.
Note on H2: Maximum power consumption used for power supply sizing. Typically encountered under fault and/or high temperature conditions.
Note on E10: All power management features are enabled in UEFI and the operating system. Server is booted to operating system and sitting idle for several minutes.
Note on F10: Typical long term power consumption under nominal conditions with no faults and user selected load factor.
Note on G10: Typical long term power consumption under nominal conditions with no faults and 100% load.
Note on H10: Maximum power consumption used for power supply sizing. Typically encountered under fault and/or high temperature conditions.
Note on E18: All power management features are enabled in UEFI and the operating system. Server is booted to operating system and sitting idle for several minutes.
Note on F18: Typical long term power consumption under nominal conditions with no faults and user selected load factor.
Note on G18: Typical long term power consumption under nominal conditions with no faults and 100% load.
Note on H18: Maximum power consumption used for power supply sizing. Typically encountered under fault and/or high temperature conditions.
Note on E26: All power management features are enabled in UEFI and the operating system. Server is booted to operating system and sitting idle for several minutes.
Note on F26: Typical long term power consumption under nominal conditions with no faults and user selected load factor.
Note on G26: Typical long term power consumption under nominal conditions with no faults and 100% load.
Note on H26: Maximum power consumption used for power supply sizing. Typically encountered under fault and/or high temperature conditions.
Note on E34: All power management features are enabled in UEFI and the operating system. Server is booted to operating system and sitting idle for several minutes.
Note on F34: Typical long term power consumption under nominal conditions with no faults and user selected load factor.
Note on G34: Typical long term power consumption under nominal conditions with no faults and 100% load.
Note on H34: Maximum power consumption used for power supply sizing. Typically encountered under fault and/or high temperature conditions.
Note on E42: All power management features are enabled in UEFI and the operating system. Server is booted to operating system and sitting idle for several minutes.
Note on F42: Typical long term power consumption under nominal conditions with no faults and user selected load factor.
Note on G42: Typical long term power consumption under nominal conditions with no faults and 100% load.
Note on H42: Maximum power consumption used for power supply sizing. Typically encountered under fault and/or high temperature conditions.
Note on E50: All power management features are enabled in UEFI and the operating system. Server is booted to operating system and sitting idle for several minutes.
Note on F50: Typical long term power consumption under nominal conditions with no faults and user selected load factor.
Note on G50: Typical long term power consumption under nominal conditions with no faults and 100% load.
Note on H50: Maximum power consumption used for power supply sizing. Typically encountered under fault and/or high temperature conditions.

## SR675V3 8 x H100 NVL 94GB
Server 1 : ThinkSystem SR675 V3 with 8 x H100 NVL 94GB
System Level Data | Total System Power (W AC Nominal Max) | 4483.7
| HVAC W AC needed for DC Air Cooling** | 1313.7241
| Total W AC Power Per System (System + HVAC) | 5797.4241
Energy Consumption | kWh / day (includes Server + DC HVAC) | 139.1382
| kWh / month (includes Server + DC HVAC) | 4174.1454
| kWh / year (includes Server + DC HVAC) | 50785.4351
Energy Cost | Power cost / day (Server + DC HVAC) @ $0.15 kWh | 20.8707
| Power cost / month (Server + DC HVAC) @ $0.15 kWh | 626.1218
| Power cost / year (Server + DC HVAC) @ $0.15 kWh | 7617.8153

## SR675V3 8 x H200 NVL 141GB
Server 2 : ThinkSystem SR675 V3 with 8 x H200 NVL 141GB
System Level Data | Total System Power (W AC Nominal Max) | 7622.3
| HVAC W AC needed for DC Air Cooling** | 2233.3339
| Total W AC Power Per System (System + HVAC) | 9855.6339
Energy Consumption | kWh / day (includes Server + DC HVAC) | 236.5352
| kWh / month (includes Server + DC HVAC) | 7096.0564
| kWh / year (includes Server + DC HVAC) | 86335.353
Energy Cost | Power cost / day (Server + DC HVAC) @ $0.15 kWh | 35.4803
| Power cost / month (Server + DC HVAC) @ $0.15 kWh | 1064.4085
| Power cost / year (Server + DC HVAC) @ $0.15 kWh | 12950.3029

## SR675V3 4 x H100 NVL 94GB
Server 3 : ThinkSystem SR675 V3 with 4 x H100 NVL 94GB PCIe
System Level Data | Total System Power (W AC Nominal Max) | 2593.8
| HVAC W AC needed for DC Air Cooling** | 759.9834
| Total W AC Power Per System (System + HVAC) | 3353.7834
Energy Consumption | kWh / day (includes Server + DC HVAC) | 80.4908
| kWh / month (includes Server + DC HVAC) | 2414.724
| kWh / year (includes Server + DC HVAC) | 29379.1426
Energy Cost | Power cost / day (Server + DC HVAC) @ $0.15 kWh | 12.0736
| Power cost / month (Server + DC HVAC) @ $0.15 kWh | 362.2086
| Power cost / year (Server + DC HVAC) @ $0.15 kWh | 4406.8714

## SR675V3 8 x L40 48GB
Server 4 : ThinkSystem SR675 V3 with 8 x L40 48GB
System Level Data | Total System Power (W AC Nominal Max) | 3210
| HVAC W AC needed for DC Air Cooling** | 940.53
| Total W AC Power Per System (System + HVAC) | 4150.53
Energy Consumption | kWh / day (includes Server + DC HVAC) | 99.6127
| kWh / month (includes Server + DC HVAC) | 2988.3816
| kWh / year (includes Server + DC HVAC) | 36358.6428
Energy Cost | Power cost / day (Server + DC HVAC) @ $0.15 kWh | 14.9419
| Power cost / month (Server + DC HVAC) @ $0.15 kWh | 448.2572
| Power cost / year (Server + DC HVAC) @ $0.15 kWh | 5453.7964

## SR650V3 16C 1 x L40S 48GB
Server 5 : ThinkSystem SR650V3 with 1 x L40S
System Level Data | Total System Power (W AC Nominal Max) | 1083.7
| HVAC W AC needed for DC Air Cooling** | 317.5241
| Total W AC Power Per System (System + HVAC) | 1401.2241
Energy Consumption | kWh / day (includes Server + DC HVAC) | 33.6294
| kWh / month (includes Server + DC HVAC) | 1008.8814
| kWh / year (includes Server + DC HVAC) | 12274.7231
Energy Cost | Power cost / day (Server + DC HVAC) @ $0.15 kWh | 5.0444
| Power cost / month (Server + DC HVAC) @ $0.15 kWh | 151.3322
| Power cost / year (Server + DC HVAC) @ $0.15 kWh | 1841.2085

## SR650V3 32C 1 x L40S 48GB
Server 6: ThinkSystem SR650V3 32C with 1 x L40S
System Level Data | Total System Power (W AC Nominal Max) | 1356.7
| HVAC W AC needed for DC Air Cooling** | 397.5131
| Total W AC Power Per System (System + HVAC) | 1754.2131
Energy Consumption | kWh / day (includes Server + DC HVAC) | 42.1011
| kWh / month (includes Server + DC HVAC) | 1263.0334
| kWh / year (includes Server + DC HVAC) | 15366.9068
Energy Cost | Power cost / day (Server + DC HVAC) @ $0.15 kWh | 6.3152
| Power cost / month (Server + DC HVAC) @ $0.15 kWh | 189.455
| Power cost / year (Server + DC HVAC) @ $0.15 kWh | 2305.036

## SR650aV4 4xL40S 48 GB
Server 7: ThinkSystem SR650a V4 with 48C 1xL40S 48GB
System Level Data | Total System Power (W AC Nominal Max) | 2297.8
| HVAC W AC needed for DC Air Cooling** | 673.2554
| Total W AC Power Per System (System + HVAC) | 2971.0554
Energy Consumption | kWh / day (includes Server + DC HVAC) | 71.3053
| kWh / month (includes Server + DC HVAC) | 2139.1599
| kWh / year (includes Server + DC HVAC) | 26026.4453
Energy Cost | Power cost / day (Server + DC HVAC) @ $0.15 kWh | 10.6958
| Power cost / month (Server + DC HVAC) @ $0.15 kWh | 320.874
| Power cost / year (Server + DC HVAC) @ $0.15 kWh | 3903.9668

## Summary
|  | Server 1 | Server 2 | Server 3 | Server 4 | Server 5 | Server 6
System Level Data | Total System Power (W AC Nominal Max) | 4483.7 | 7622.3 | 2593.8 | 3210 | 1083.7 | 1356.7
| HVAC W AC needed for DC Air Cooling** | 1313.7241 | 2233.3339 | 759.9834 | 940.53 | 317.5241 | 397.5131
| Total W AC Power Per System (System + HVAC) | 5797.4241 | 9855.6339 | 3353.7834 | 4150.53 | 1401.2241 | 1754.2131
Energy Consumption | kWh / day (includes Server + DC HVAC) | 139.1382 | 236.5352 | 80.4908 | 99.6127 | 33.6294 | 42.1011
| kWh / month (includes Server + DC HVAC) | 4174.1454 | 7096.0564 | 2414.724 | 2988.3816 | 1008.8814 | 1263.0334
| kWh / year (includes Server + DC HVAC) | 50785.4351 | 86335.353 | 29379.1426 | 36358.6428 | 12274.7231 | 15366.9068
Energy Cost | Power cost / day (Server + DC HVAC) @ $0.15 kWh | 20.8707 | 35.4803 | 12.0736 | 14.9419 | 5.0444 | 6.3152
| Power cost / month (Server + DC HVAC) @ $0.15 kWh | 626.1218 | 1064.4085 | 362.2086 | 448.2572 | 151.3322 | 189.455
| Power cost / year (Server + DC HVAC) @ $0.15 kWh | 7617.8153 | 12950.3029 | 4406.8714 | 5453.7964 | 1841.2085 | 2305.036